## Recommended_CEM_Base
Recommended ERCOT CEM Base — Technology-Specific Sources (Real 2025$)
Recommended hybrid base: ERCOT LTSA for gas / ICE / SMR / solar and 2h/6h storage; NLR/NREL ATB Moderate Wind Class 1 for onshore wind; NLR 2025 Mid for 4-hour battery CAPEX. O&M remains from EIA or ATB where the CAPEX source does not provide a directly comparable O&M series.
Technology | Economic life (yr) | Real WACC | 2030 CAPEX (2025$/kW) | CRF | 2030 annualized CAPEX (2025$/kW-yr) | 2030 FOM (2025$/kW-yr) | 2030 total fixed (2025$/kW-yr) | VOM (2025$/MWh) | Heat rate (Btu/kWh) | 2035 CAPEX (2025$/kW) | 2035 annualized CAPEX (2025$/kW-yr) | 2035 FOM (2025$/kW-yr) | 2035 total fixed (2025$/kW-yr) | CAPEX source | O&M source | Modeling note
CC multi-shaft | 30 | 7% | 1314.8599 | 0.080586 | 105.9598 | 12.69 | 118.6498 | 3.57 | 6226 | 1254.1144 | 101.0646 | 12.69 | 113.7546 | ERCOT 2026 LTSA | EIA AEO2026; held constant in real 2025$ unless changed | Recommended base = ERCOT LTSA CAPEX; EIA TRE is a lower current regional anchor, not a 2030/2035 forecast.
Advanced CT | 30 | 7% | 1193.778 | 0.080586 | 96.2023 | 7.18 | 103.3823 | 4.17 | 9142 | 1109.3161 | 89.3958 | 7.18 | 96.5758 | ERCOT 2026 LTSA | EIA AEO2026; held constant in real 2025$ unless changed | Recommended base = ERCOT LTSA CAPEX; EIA industrial-frame CT provides the current Texas regional anchor.
ICE | 30 | 7% | 2102.3408 | 0.080586 | 169.4201 |  | 169.4201 |  |  | 2036.8298 | 164.1408 |  | 164.1408 | ERCOT 2026 LTSA | Not populated — add engine-specific O&M/performance source | ICE = reciprocating internal-combustion engine. Keep optional unless flexible engine capacity is explicitly represented; engine-specific O&M/heat rate still needed.
SMR | 60 | 7% | 8608.4759 | 0.071229 | 613.1751 | 127.62 | 740.7951 | 3.32 | 10445 | 8133.6439 | 579.3532 | 127.62 | 706.9732 | ERCOT 2026 LTSA | EIA AEO2026; held constant in real 2025$ unless changed | Recommended central SMR CAPEX = ERCOT LTSA, but cost uncertainty is very large; retain ATB Advanced and Conservative cases as explicit low/high sensitivities.
Wind | 30 | 7% | 1548.8568 | 0.080586 | 124.8168 | 32.1924 | 157.0092 | 0 |  | 1468.2638 | 118.3221 | 31.0895 | 149.4116 | NLR/NREL ATB 2024b Moderate — Wind Class 1 | NLR/NREL ATB 2024b Moderate | Recommended base uses ATB Moderate Class 1 because ERCOT LTSA wind CAPEX is materially above ATB and recent ERCOT LBNL actuals; ERCOT LTSA is retained as a conservative/high benchmark.
Solar | 30 | 7% | 1171.3554 | 0.080586 | 94.3953 | 23.6 | 117.9953 | 0 |  | 1052.2012 | 84.7931 | 23.6 | 108.3931 | ERCOT 2026 LTSA | EIA AEO2026; held constant in real 2025$ unless changed | Recommended base = ERCOT LTSA solar CAPEX; ATB/EIA are relatively close and remain useful sensitivities/checks.
BESS 2h | 15 | 7% | 697.7906 | 0.10979 | 76.6137 | 22.2427 | 98.8563 | 0 |  | 645.157 | 70.8348 | 20.7136 | 91.5484 | ERCOT 2026 LTSA | NLR/NREL ATB Moderate duration-specific O&M | 2-hour BESS remains an alternate-duration option; recommended CAPEX = ERCOT LTSA because the newer NLR 2025 projection is specifically used here for 4-hour storage.
BESS 4h | 15 | 7% | 1145.365 | 0.10979 | 125.7549 | 35.7567 | 161.5116 | 0 |  | 997.5759 | 109.5285 | 32.9995 | 142.5279 | NLR 2025 Utility-Scale Battery Storage — Mid | NLR/NREL ATB 2024b Moderate duration-specific O&M | Recommended 4-hour BESS CAPEX uses the newer NLR 2025 Mid trajectory; use NLR Low/High as the preferred battery cost sensitivities.
BESS 6h | 15 | 7% | 1705.0128 | 0.10979 | 187.2012 | 49.2707 | 236.472 | 0 |  | 1576.6929 | 173.1124 | 45.2854 | 218.3978 | ERCOT 2026 LTSA | NLR/NREL ATB Moderate duration-specific O&M | 6-hour BESS remains an alternate-duration option; recommended CAPEX = ERCOT LTSA because the newer NLR 2025 projection is specifically used here for 4-hour storage.
Annualization method
CRF = r(1+r)^n / [(1+r)^n - 1]. Annualized CAPEX = real-2025$ CAPEX × CRF. Total fixed = annualized CAPEX + FOM.
The 7% real WACC and economic lives are editable assumptions on the Assumptions sheet; they are not source facts.
For direct CEM import, the 2030 columns D/F/G/H/I/J and 2035 columns K/L/M/N are the main outputs.
Recommended CAPEX Sensitivity Anchors — Real 2025$/kW
Technology | 2030 Low | 2030 Base | 2030 High | 2035 Low | 2035 Base | 2035 High | Guidance
SMR | 7058.9076 | 8608.4759 | 13950.2145 | 4222.7394 | 8133.6439 | 13259.6098 | Low = ATB Advanced; Base = ERCOT LTSA; High = ATB Conservative. Treat as a wide scenario range, not a tight confidence interval.
Wind | 1475.9427 | 1548.8568 | 2010.8567 | 1384.776 | 1468.2638 | 1960.4085 | Low = ATB Advanced Class 1; Base = ATB Moderate Class 1; High = ERCOT LTSA planning assumption. LBNL ERCOT actual cost remains an empirical calibration.
BESS 4h | 849.7869 | 1145.365 | 1453.2588 | 603.4719 | 997.5759 | 1391.68 | Low/Base/High = NLR 2025 Low/Mid/High trajectories; this is the preferred storage cost sensitivity family.

## Assumptions
ERCOT CEM Technology-Cost Workbook — Conversion & Annualization Assumptions
Assumption | Value | Unit | Use | Editable? | Source / note
ERCOT LTSA nominal inflation | 2.2% | %/yr | Deflate ERCOT future nominal costs back to 2025$ | Yes | ERCOT 2026 LTSA
Real discount rate / WACC | 7% | % | Annualize CAPEX with a capital recovery factor | Yes | Modeling default — change to your CEM convention
Base dollar year | 2025 | year | Common comparison dollar year | Yes | User requested 2025$
Dollar year | CPI-U annual average | 2025$/source-$ factor | Source URL
2022 | 292.655 | 1.1001 | https://www.bls.gov/regions/northeast/data/consumerpriceindex_us_table.htm
2023 | 304.702 | 1.0566 | https://www.bls.gov/regions/northeast/data/consumerpriceindex_us_table.htm
2024 | 313.689 | 1.0263 | https://www.bls.gov/regions/northeast/data/consumerpriceindex_us_table.htm
2025 | 321.943 | 1 | https://www.bls.gov/regions/northeast/data/consumerpriceindex_us_table.htm
Technology | Economic life (yr) | Note
CC multi-shaft | 30 | Editable CEM annualization assumption
Advanced CT | 30 | Editable CEM annualization assumption
ICE | 30 | Editable CEM annualization assumption
SMR | 60 | Editable CEM annualization assumption
Wind | 30 | Editable CEM annualization assumption
Solar | 30 | Editable CEM annualization assumption
BESS 2h | 15 | Editable CEM annualization assumption
BESS 4h | 15 | Editable CEM annualization assumption
BESS 6h | 15 | Editable CEM annualization assumption
Conversion methodology
2022/2023/2024 source-dollar values are converted to 2025$ using annual-average U.S. CPI-U ratios.
Future ERCOT nominal values are deflated using ERCOT's stated 2.2% annual inflation assumption, rather than CPI.
The 7% WACC and economic lives are modeling assumptions, not raw source facts. Both are editable.

## README_Sources
ERCOT Capacity-Expansion Technology Cost Assumptions — 2030 / 2035
Source | Role in workbook | Geography | Dollar basis | Projection status | Why useful for ERCOT | URL
ERCOT 2026 LTSA — Current Trends | Primary base CAPEX | ERCOT | Nominal future $; converted to 2025$ | 2027–2041 annual series | ERCOT's own CEM/planning assumptions | https://www.ercot.com/files/docs/2025/12/15/2026-LTSA-Update-Current-Trends-Capacity-Expansion-Results.pdf
EIA AEO2026 Electricity Market Module | Regional cost/O&M benchmark | TRE = Texas | 2025$ | Initial/current new-build cost anchor | Texas regional multipliers + updated gas turbine costs | https://www.eia.gov/outlooks/aeo/assumptions/pdf/EMM_Assumptions.pdf
NLR/NREL 2024b ATB v4 | Technology-learning sensitivity | U.S. / resource classes | 2022$ | 2030/2035 Advanced / Moderate / Conservative | Transparent long-run technology learning cases | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
NLR Utility-Scale Battery Storage 2025 Update | Battery-specific sensitivity | U.S. | 2024$ | Annual future projections | More current storage learning than frozen 2024 ATB | https://www.nlr.gov/docs/fy25osti/93281.pdf
Berkeley Lab Land-Based Wind Market Report 2024 | Empirical calibration | ERCOT | 2023$ | Historical actual 2022–2023 projects | Direct ERCOT observed project-cost benchmark | https://emp.lbl.gov/sites/default/files/2024-08/Land-Based%20Wind%20Market%20Report_2024%20Edition.pdf
Berkeley Lab Utility-Scale Solar 2025 | Empirical calibration | U.S. | 2024$ | Historical actual 2024 projects | Observed utility-scale PV benchmark; not ERCOT-specific | https://emp.lbl.gov/publications/us-utility-scale-solar-2025-data
BLS CPI-U | Dollar-year conversion | U.S. | Index | Historical | Transparent conversion to 2025 dollars | https://www.bls.gov/regions/northeast/data/consumerpriceindex_us_table.htm
Lazard LCOE+ v18 | Underlying/secondary benchmark | U.S. | Varies | Market benchmark | Cited by ERCOT LTSA as an input source; not separately harmonized | https://www.lazard.com/research-insights/levelized-cost-of-energyplus/
Recommended interpretation
Base case | Use the technology-specific hybrid in Recommended_CEM_Base: ERCOT LTSA for gas/ICE/SMR/solar and 2h/6h BESS; ATB Moderate Class 1 for wind; NLR 2025 Mid for 4h BESS.
Cross-check | Use EIA TRE/Texas as a current regional anchor; do not relabel it as an explicit 2030/2035 forecast.
Learning sensitivities | Wind: ATB Advanced / Moderate with ERCOT LTSA as conservative planning benchmark. 4h BESS: NLR 2025 Low/Mid/High. SMR: ATB Advanced / ERCOT / ATB Conservative.
Empirical calibration | Use LBNL actual wind/solar costs as a reality check, not as forward projections.
Annualization | Recommended_CEM_Base applies the editable real WACC/life and then adds FOM; HOPE_CostProfiles converts the recommended fixed cost to $/MW-yr.
Workbook navigation | Recommended_CEM_Base = preferred hybrid inputs; CEM_BaseCase = all-ERCOT-LTSA benchmark; HOPE_CostProfiles = HOPE-formatted recommended costs.
HOPE model-input format references (from current GitHub project)
HOPE candidate cost profile | candidate_resource_costs_2035.csv | Current HOPE project format | Stores CAPEX/FOM/FCR plus final $/MW-yr and $/MWh | Used by the case builder | HOPE_CostProfiles follows this schema in columns A:U | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv
HOPE generation candidates | gendata_candidate.csv | Current HOPE project format | Direct model input | Project/zone/build limit + fixed/variable cost + reliability/emissions | HOPE_GenCandidate follows the exact model columns in A:Y | https://github.com/swang22/PJM_DC_health_study_project/blob/main/ModelCases/PJM_ICARUS21_GTEP_2035_Base_case/Data_PJM_ICARUS21_GTEP_2035_Base/gendata_candidate.csv
HOPE storage candidates | storagedata_candidate.csv | Current HOPE project format | Direct model input | Energy/power capacity + efficiency + fixed/variable cost + CC | HOPE_StorageCandidate follows the exact model columns in A:V | https://github.com/swang22/PJM_DC_health_study_project/blob/main/ModelCases/PJM_ICARUS21_GTEP_2035_Base_case/Data_PJM_ICARUS21_GTEP_2035_Base/storagedata_candidate.csv

## ERCOT_LTSA_2026
ERCOT 2026 LTSA — New Unit Capital Costs
Source: | https://www.ercot.com/files/docs/2025/12/15/2026-LTSA-Update-Current-Trends-Capacity-Expansion-Results.pdf
Raw source values — nominal $/kW
Year | CC multi-shaft | Advanced CT | ICE | SMR | Wind | Solar | BESS 2h | BESS 4h | BESS 6h
| nominal $/kW | nominal $/kW | nominal $/kW | nominal $/kW | nominal $/kW | nominal $/kW | nominal $/kW | nominal $/kW | nominal $/kW
2027 | 1436 | 1325 | 2236 | 9439 | 2165 | 1308 | 782 | 1347 | 1912
2028 | 1439 | 1319 | 2272 | 9450 | 2180 | 1289 | 770 | 1326 | 1882
2029 | 1449 | 1321 | 2308 | 9509 | 2207 | 1296 | 772 | 1329 | 1887
2030 | 1466 | 1331 | 2344 | 9598 | 2242 | 1306 | 778 | 1339 | 1901
2031 | 1487 | 1344 | 2379 | 9716 | 2284 | 1307 | 786 | 1352 | 1920
2032 | 1508 | 1357 | 2417 | 9831 | 2325 | 1311 | 789 | 1359 | 1929
2033 | 1529 | 1369 | 2456 | 9938 | 2365 | 1313 | 795 | 1368 | 1942
2034 | 1540 | 1364 | 2494 | 10033 | 2403 | 1312 | 798 | 1374 | 1950
2035 | 1559 | 1379 | 2532 | 10111 | 2437 | 1308 | 802 | 1381 | 1960
2036 | 1581 | 1395 | 2568 | 10201 | 2475 | 1308 | 806 | 1387 | 1969
2037 | 1606 | 1415 | 2606 | 10311 | 2518 | 1317 | 810 | 1394 | 1979
2038 | 1633 | 1437 | 2645 | 10425 | 2563 | 1328 | 814 | 1402 | 1990
2039 | 1660 | 1460 | 2684 | 10535 | 2608 | 1344 | 819 | 1410 | 2002
2040 | 1688 | 1482 | 2725 | 10647 | 2654 | 1361 | 825 | 1420 | 2016
2041 | 1714 | 1502 | 2766 | 10760 | 2700 | 1376 | 829 | 1428 | 2027
Converted values — real 2025$/kW
Year | CC multi-shaft | Advanced CT | ICE | SMR | Wind | Solar | BESS 2h | BESS 4h | BESS 6h
| 2025$/kW | 2025$/kW | 2025$/kW | 2025$/kW | 2025$/kW | 2025$/kW | 2025$/kW | 2025$/kW | 2025$/kW
2027 | 1374.8415 | 1268.569 | 2140.77 | 9036.9982 | 2072.7938 | 1252.293 | 748.695 | 1289.632 | 1830.569
2028 | 1348.0565 | 1235.6404 | 2128.4117 | 8852.7688 | 2042.226 | 1207.5364 | 721.3367 | 1242.198 | 1763.0593
2029 | 1328.2041 | 1210.8748 | 2115.5935 | 8716.2818 | 2023.0134 | 1187.9589 | 707.6422 | 1218.2079 | 1729.6902
2030 | 1314.8599 | 1193.778 | 2102.3408 | 8608.4759 | 2010.8567 | 1171.3554 | 697.7906 | 1200.9532 | 1705.0128
2031 | 1304.9852 | 1179.489 | 2087.8008 | 8526.7225 | 2004.4292 | 1147.0179 | 689.7904 | 1186.5098 | 1684.9843
2032 | 1294.9264 | 1165.262 | 2075.4887 | 8441.9238 | 1996.4879 | 1125.7616 | 677.5178 | 1166.9794 | 1656.4409
2033 | 1284.6958 | 1150.2607 | 2063.5795 | 8350.1029 | 1987.1195 | 1103.2084 | 667.9746 | 1149.4205 | 1631.7066
2034 | 1266.0844 | 1121.389 | 2050.399 | 8248.4577 | 1975.5849 | 1078.6381 | 656.0619 | 1129.6104 | 1603.1588
2035 | 1254.1144 | 1109.3161 | 2036.8298 | 8133.6439 | 1960.4085 | 1052.2012 | 645.157 | 1110.9249 | 1576.6929
2036 | 1244.4344 | 1098.0304 | 2021.3204 | 8029.3963 | 1948.1184 | 1029.5511 | 634.4175 | 1091.7334 | 1549.8364
2037 | 1236.9006 | 1089.7972 | 2007.0753 | 7941.2714 | 1939.2999 | 1014.3201 | 623.8415 | 1073.6235 | 1524.1757
2038 | 1230.6216 | 1082.9169 | 1993.2604 | 7856.2341 | 1931.4655 | 1000.775 | 613.4268 | 1056.541 | 1499.6552
2039 | 1224.0398 | 1076.5651 | 1979.1102 | 7768.2286 | 1923.0698 | 991.0298 | 603.9088 | 1039.6965 | 1476.2215
2040 | 1217.8926 | 1069.2636 | 1966.0885 | 7681.8145 | 1914.862 | 981.962 | 595.2378 | 1024.5305 | 1454.5448
2041 | 1210.031 | 1060.3655 | 1952.7104 | 7596.2271 | 1906.1165 | 971.4134 | 585.2483 | 1008.1238 | 1430.9993
Notes
ERCOT's source table is nominal $/kW; the 2025$ table uses ERCOT's 2.2% annual inflation assumption.
These are the preferred ERCOT-specific base-case new-build CAPEX assumptions in this workbook.
FOM/VOM are not supplied in this LTSA capital-cost table; see EIA and ATB sheets.

## EIA_AEO2026_TRE
EIA AEO2026 — New-Build Cost & Performance Assumptions (TRE / Texas)
Source: | https://www.eia.gov/outlooks/aeo/assumptions/pdf/EMM_Assumptions.pdf
Technology | First available year | Size (MW) | Lead time (yr) | Base overnight cost (2025$/kW) | Total overnight cost (2025$/kW) | TRE regional overnight cost (2025$/kW) | FOM (2025$/kW-yr) | VOM (2025$/MWh) | Heat rate / EIA convention (Btu/kWh) | Notes | Source URL
CC single-shaft | 2028 | 627 | 3 | 1086 | 1086 | 980 | 16.23 | 3.49 | 6226 | TRE = Texas Reliability Entity | https://www.eia.gov/outlooks/aeo/assumptions/pdf/EMM_Assumptions.pdf
CC multi-shaft | 2028 | 1227 | 3 | 1032 | 1032 | 930 | 12.69 | 3.57 | 6226 | Preferred EIA comparator for ERCOT CC | https://www.eia.gov/outlooks/aeo/assumptions/pdf/EMM_Assumptions.pdf
CC with 95% CCS | 2029 | 543 | 4 | 2567 | 2824 | 2504 | 25.93 | 5.29 | 7239 |  | https://www.eia.gov/outlooks/aeo/assumptions/pdf/EMM_Assumptions.pdf
CT aeroderivative | 2027 | 211 | 2 | 2275 | 2275 | 2058 | 9.99 | 5.97 | 9447 |  | https://www.eia.gov/outlooks/aeo/assumptions/pdf/EMM_Assumptions.pdf
CT industrial frame | 2027 | 419 | 2 | 1158 | 1158 | 1033 | 7.18 | 4.17 | 9142 | Preferred EIA comparator for ERCOT CT | https://www.eia.gov/outlooks/aeo/assumptions/pdf/EMM_Assumptions.pdf
Nuclear - large LWR | 2031 | 2156 | 6 | 7862 | 8255 | 7866 | 163.4 | 2.62 | 10445 |  | https://www.eia.gov/outlooks/aeo/assumptions/pdf/EMM_Assumptions.pdf
Nuclear - SMR | 2031 | 480 | 6 | 8937 | 9831 | 9366 | 127.62 | 3.32 | 10445 |  | https://www.eia.gov/outlooks/aeo/assumptions/pdf/EMM_Assumptions.pdf
Battery storage - 4h Li-ion | 2026 | 150 | 1 | 1521 | 1521 | 1500 | 41.84 | 0 |  | EIA defines battery storage as four-hour Li-ion | https://www.eia.gov/outlooks/aeo/assumptions/pdf/EMM_Assumptions.pdf
Wind - onshore | 2028 | 200 | 3 | 1712 | 1712 | 1562 | 34.57 | 0 | 3412 | 3,412 is EIA primary-energy heat-content convention, not a thermal efficiency | https://www.eia.gov/outlooks/aeo/assumptions/pdf/EMM_Assumptions.pdf
Solar PV - tracking | 2027 | 150 | 2 | 1484 | 1484 | 1342 | 23.6 | 0 | 3412 | Costs/capacity expressed on an AC basis | https://www.eia.gov/outlooks/aeo/assumptions/pdf/EMM_Assumptions.pdf
Solar PV + storage | 2027 | 150 | 2 | 1903 | 1903 | 1840 | 40 | 0 | 3412 | 150 MW PV + 50 MW four-hour battery | https://www.eia.gov/outlooks/aeo/assumptions/pdf/EMM_Assumptions.pdf
Interpretation
TRE is EIA region 1, Texas Reliability Entity. Use the TRE cost as a regional cross-check, not as an explicit EIA 2030/2035 point.
AEO2026 updated CC/CT inputs for recent turbine, materials, and labor tightness and applies regional/locality adjustments.
EIA explicitly represents battery storage as a four-hour lithium-ion battery.

## NLR_ATB_2024b
NLR/NREL 2024b ATB v4 — 2030 / 2035 Cost Scenarios
Source workbook: | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
Technology | ATB detail | Scenario | CRP years | CAPEX 2030 (2022$/kW) | CAPEX 2035 (2022$/kW) | FOM 2030 (2022$/kW-yr) | FOM 2035 (2022$/kW-yr) | VOM 2030 (2022$/MWh) | VOM 2035 (2022$/MWh) | CAPEX 2030 (2025$/kW) | CAPEX 2035 (2025$/kW) | FOM 2030 (2025$/kW-yr) | FOM 2035 (2025$/kW-yr) | VOM 2030 (2025$/MWh) | VOM 2035 (2025$/MWh) | Source URL
CC F-frame | NG 2-on-1 Combined Cycle (F-Frame) | Advanced | 30 | 1381.1314 | 1307.2497 | 30.7 | 28.3 | 2 | 1.89 | 1519.3508 | 1438.0752 | 33.7724 | 31.1322 | 2.2002 | 2.0791 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
CC F-frame | NG 2-on-1 Combined Cycle (F-Frame) | Moderate | 30 | 1403.3071 | 1343.3548 | 31.8 | 30.1 | 2.04 | 1.96 | 1543.7457 | 1477.7936 | 34.9824 | 33.1123 | 2.2442 | 2.1562 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
CC F-frame | NG 2-on-1 Combined Cycle (F-Frame) | Conservative | 30 | 1425.4828 | 1379.3485 | 32.8 | 31.8 | 2.08 | 2.03 | 1568.1406 | 1517.3894 | 36.0825 | 34.9824 | 2.2882 | 2.2332 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
CT F-frame | NG Combustion Turbine (F-Frame) | Advanced | 30 | 1270.476 | 1221.4444 | 25 | 24.2 | 6.94 | 6.94 | 1397.6213 | 1343.6827 | 27.5019 | 26.6219 | 7.6345 | 7.6345 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
CT F-frame | NG Combustion Turbine (F-Frame) | Moderate | 30 | 1270.476 | 1221.4444 | 25 | 24.2 | 6.94 | 6.94 | 1397.6213 | 1343.6827 | 27.5019 | 26.6219 | 7.6345 | 7.6345 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
CT F-frame | NG Combustion Turbine (F-Frame) | Conservative | 30 | 1270.476 | 1221.4444 | 25 | 24.2 | 6.94 | 6.94 | 1397.6213 | 1343.6827 | 27.5019 | 26.6219 | 7.6345 | 7.6345 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
SMR | Nuclear - Small | Advanced | 30 | 6416.7403 | 3838.5857 | 118 | 118 | 2.2 | 2.2 | 7058.9076 | 4222.7394 | 129.8091 | 129.8091 | 2.4202 | 2.4202 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
SMR | Nuclear - Small | Moderate | 30 | 9650.0007 | 7862.9635 | 136 | 136 | 2.6 | 2.6 | 10615.7427 | 8649.8644 | 149.6105 | 149.6105 | 2.8602 | 2.8602 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
SMR | Nuclear - Small | Conservative | 30 | 12681.1268 | 12053.3483 | 216 | 216 | 2.8 | 2.8 | 13950.2145 | 13259.6098 | 237.6166 | 237.6166 | 3.0802 | 3.0802 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
Wind class 1 | Land-Based Wind - Class 1 - Technology 1 | Advanced | 30 | 1341.6723 | 1258.7993 | 26.3145 | 23.8344 | 0 | 0 | 1475.9427 | 1384.776 | 28.9479 | 26.2197 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
Wind class 1 | Land-Based Wind - Class 1 - Technology 1 | Moderate | 30 | 1407.9532 | 1334.692 | 29.2638 | 28.2612 | 0 | 0 | 1548.8568 | 1468.2638 | 32.1924 | 31.0895 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
Wind class 1 | Land-Based Wind - Class 1 - Technology 1 | Conservative | 30 | 1577.3918 | 1522.1515 | 30.9109 | 30.2909 | 0 | 0 | 1735.2522 | 1674.4837 | 34.0044 | 33.3223 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
Wind class 7 | Land-Based Wind - Class 7 - Technology 1 | Advanced | 30 | 1341.6723 | 1258.7993 | 26.3145 | 23.8344 | 0 | 0 | 1475.9427 | 1384.776 | 28.9479 | 26.2197 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
Wind class 7 | Land-Based Wind - Class 7 - Technology 1 | Moderate | 30 | 1472.8514 | 1383.3656 | 29.2638 | 28.2612 | 0 | 0 | 1620.2498 | 1521.8085 | 32.1924 | 31.0895 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
Wind class 7 | Land-Based Wind - Class 7 - Technology 1 | Conservative | 30 | 1577.3918 | 1522.1515 | 30.9109 | 30.2909 | 0 | 0 | 1735.2522 | 1674.4837 | 34.0044 | 33.3223 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
Solar PV | Utility PV - Class 1 | Advanced | 30 | 1069.5665 | 682.8964 | 16.6388 | 12.7638 | 0 | 0 | 1176.6054 | 751.2385 | 18.304 | 14.0412 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
Solar PV | Utility PV - Class 1 | Moderate | 30 | 1193.4809 | 895.3211 | 17.9907 | 15.0217 | 0 | 0 | 1312.9208 | 984.9221 | 19.7911 | 16.525 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
Solar PV | Utility PV - Class 1 | Conservative | 30 | 1364.9377 | 1189.2471 | 19.7248 | 17.9619 | 0 | 0 | 1501.5365 | 1308.2632 | 21.6988 | 19.7595 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
BESS 2h | Utility-Scale Battery Storage - 2Hr | Advanced | * | 706.0799 | 652.792 | 14.5297 | 13.2445 | 0 | 0 | 776.7422 | 718.1214 | 15.9838 | 14.5699 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
BESS 2h | Utility-Scale Battery Storage - 2Hr | Moderate | * | 941.9756 | 884.3444 | 20.2192 | 18.8292 | 0 | 0 | 1036.2456 | 972.8469 | 22.2427 | 20.7136 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
BESS 2h | Utility-Scale Battery Storage - 2Hr | Conservative | * | 1114.4629 | 1079.859 | 24.3794 | 23.5448 | 0 | 0 | 1225.9949 | 1187.9279 | 26.8192 | 25.9011 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
BESS 4h | Utility-Scale Battery Storage - 4Hr | Advanced | * | 1117.5994 | 1028.7117 | 24.455 | 22.3112 | 0 | 0 | 1229.4452 | 1131.662 | 26.9024 | 24.544 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
BESS 4h | Utility-Scale Battery Storage - 4Hr | Moderate | * | 1451.3156 | 1347.3964 | 32.5038 | 29.9974 | 0 | 0 | 1596.5588 | 1482.2396 | 35.7567 | 32.9995 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
BESS 4h | Utility-Scale Battery Storage - 4Hr | Conservative | * | 1774.9148 | 1717.701 | 40.3086 | 38.9287 | 0 | 0 | 1952.5427 | 1889.6032 | 44.3426 | 42.8245 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
BESS 6h | Utility-Scale Battery Storage - 6Hr | Advanced | * | 1529.1188 | 1404.6315 | 34.3803 | 31.3779 | 0 | 0 | 1682.1483 | 1545.2026 | 37.821 | 34.5181 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
BESS 6h | Utility-Scale Battery Storage - 6Hr | Moderate | * | 1960.6556 | 1810.4484 | 44.7884 | 41.1656 | 0 | 0 | 2156.8719 | 1991.6324 | 49.2707 | 45.2854 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
BESS 6h | Utility-Scale Battery Storage - 6Hr | Conservative | * | 2435.3667 | 2355.543 | 56.2378 | 54.3126 | 0 | 0 | 2679.0906 | 2591.2784 | 61.8659 | 59.748 | 0 | 0 | https://data.openei.org/files/6006/2024_v4_Workbook_7-22-2026.xlsx
Notes
ATB 2024b monetary values are in 2022 dollars.
The December 2025 2024b reference refresh did not change the underlying ATB data.
Wind Classes 1 and 7 are both retained because the resource/site class choice can affect CAPEX and is relevant for ERCOT.

## NLR_BESS_2025
NLR 2025 Utility-Scale Battery Cost Projection — 4-hour Li-ion
Source: | https://www.nlr.gov/docs/fy25osti/93281.pdf
Year | Low (2024$/kWh) | Mid (2024$/kWh) | High (2024$/kWh) | Low 4h (2024$/kW) | Mid 4h (2024$/kW) | High 4h (2024$/kW) | Low 4h (2025$/kW) | Mid 4h (2025$/kW) | High 4h (2025$/kW) | Source URL
2024 | 334 | 334 | 334 | 1336 | 1336 | 1336 | 1371.1537 | 1371.1537 | 1371.1537 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2025 | 295 | 321 | 350 | 1180 | 1284 | 1400 | 1211.049 | 1317.7855 | 1436.8378 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2026 | 255 | 308 | 366 | 1020 | 1232 | 1464 | 1046.8389 | 1264.4172 | 1502.5218 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2027 | 243 | 301 | 363 | 972 | 1204 | 1452 | 997.5759 | 1235.6805 | 1490.206 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2028 | 231 | 293 | 360 | 924 | 1172 | 1440 | 948.3129 | 1202.8385 | 1477.8903 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2029 | 219 | 286 | 357 | 876 | 1144 | 1428 | 899.0499 | 1174.1017 | 1465.5745 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2030 | 207 | 279 | 354 | 828 | 1116 | 1416 | 849.7869 | 1145.365 | 1453.2588 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2031 | 195 | 272 | 351 | 780 | 1088 | 1404 | 800.5239 | 1116.6282 | 1440.943 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2032 | 183 | 265 | 348 | 732 | 1060 | 1392 | 751.2609 | 1087.8914 | 1428.6273 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2033 | 171 | 257 | 345 | 684 | 1028 | 1380 | 701.9979 | 1055.0494 | 1416.3115 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2034 | 159 | 250 | 342 | 636 | 1000 | 1368 | 652.7349 | 1026.3127 | 1403.9958 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2035 | 147 | 243 | 339 | 588 | 972 | 1356 | 603.4719 | 997.5759 | 1391.68 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2036 | 145 | 239 | 337 | 580 | 956 | 1348 | 595.2614 | 981.1549 | 1383.4695 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2037 | 142 | 234 | 335 | 568 | 936 | 1340 | 582.9456 | 960.6287 | 1375.259 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2038 | 139 | 230 | 333 | 556 | 920 | 1332 | 570.6299 | 944.2077 | 1367.0485 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2039 | 137 | 226 | 331 | 548 | 904 | 1324 | 562.4194 | 927.7867 | 1358.838 | https://www.nlr.gov/docs/fy25osti/93281.pdf
2040 | 134 | 221 | 329 | 536 | 884 | 1316 | 550.1036 | 907.2604 | 1350.6275 | https://www.nlr.gov/docs/fy25osti/93281.pdf
Notes
The report states that $/kWh can be converted to $/kW by multiplying by storage duration; this sheet uses four hours.
Use this newer series as a battery-specific sensitivity to the older ATB trajectory.

## LBNL_Actuals
Berkeley Lab — Empirical Installed-Cost Benchmarks (Calibration Only)
Technology | Region | Project/COD year(s) | Raw installed cost | Raw unit / dollar year | 2025$/kW equivalent | Use in ERCOT CEM | Notes | Source URL
Land-based wind | ERCOT | 2022–2023 | 1370 | 2023$/kW | 1447.5189 | Strong empirical ERCOT calibration | Capacity-weighted regional mean; historical, not a forward forecast | https://emp.lbl.gov/sites/default/files/2024-08/Land-Based%20Wind%20Market%20Report_2024%20Edition.pdf
Utility-scale solar PV | U.S. | 2024 | 1610 | 2024$/kW-AC | 1652.3634 | National empirical calibration | Capacity-weighted mean; preliminary 2024 sample; not ERCOT-specific | https://emp.lbl.gov/publications/us-utility-scale-solar-2025-data
Important
These are observed installed-cost benchmarks. Do not treat them as 2030/2035 projections.
The ERCOT wind value is especially useful for diagnosing whether a future wind CAPEX path is too conservative.

## Compare_2030_2035
Harmonized CAPEX Comparison — All Values in Real 2025$/kW
Technology | ERCOT LTSA 2030 | ATB Moderate 2030 | ATB Advanced 2030 | ATB Conservative 2030 | EIA TRE current anchor | NLR BESS Mid 2030 | LBNL empirical anchor | ERCOT LTSA 2035 | ATB Moderate 2035 | ATB Advanced 2035 | ATB Conservative 2035 | NLR BESS Mid 2035 | Interpretation | Recommended Base 2030 | Recommended Base 2035 | Recommended Base Source
CC multi-shaft | 1314.8599 | 1543.7457 | 1519.3508 | 1568.1406 | 930 |  |  | 1254.1144 | 1477.7936 | 1438.0752 | 1517.3894 |  | Recommended base = ERCOT LTSA; EIA is a lower current regional anchor. | 1314.8599 | 1254.1144 | ERCOT 2026 LTSA
Advanced CT | 1193.778 | 1397.6213 | 1397.6213 | 1397.6213 | 1033 |  |  | 1109.3161 | 1343.6827 | 1343.6827 | 1343.6827 |  | Recommended base = ERCOT LTSA; compare with EIA industrial-frame CT. | 1193.778 | 1109.3161 | ERCOT 2026 LTSA
SMR | 8608.4759 | 10615.7427 | 7058.9076 | 13950.2145 | 9366 |  |  | 8133.6439 | 8649.8644 | 4222.7394 | 13259.6098 |  | Recommended central = ERCOT LTSA; retain wide ATB low/high sensitivity. | 8608.4759 | 8133.6439 | ERCOT 2026 LTSA
Wind | 2010.8567 | 1548.8568 | 1475.9427 | 1735.2522 | 1562 |  | 1447.5189 | 1960.4085 | 1468.2638 | 1384.776 | 1674.4837 |  | Recommended base = ATB Moderate Class 1; ERCOT LTSA = conservative/high planning benchmark. | 1548.8568 | 1468.2638 | NLR/NREL ATB 2024b Moderate — Wind Class 1
Solar | 1171.3554 | 1312.9208 | 1176.6054 | 1501.5365 | 1342 |  | 1652.3634 | 1052.2012 | 984.9221 | 751.2385 | 1308.2632 |  | Recommended base = ERCOT LTSA; source disagreement is comparatively modest. | 1171.3554 | 1052.2012 | ERCOT 2026 LTSA
BESS 2h | 697.7906 | 1036.2456 | 776.7422 | 1225.9949 |  |  |  | 645.157 | 972.8469 | 718.1214 | 1187.9279 |  | Recommended base = ERCOT LTSA; alternate duration, while 4h remains the preferred core storage case. | 697.7906 | 645.157 | ERCOT 2026 LTSA
BESS 4h | 1200.9532 | 1596.5588 | 1229.4452 | 1952.5427 | 1500 | 1145.365 |  | 1110.9249 | 1482.2396 | 1131.662 | 1889.6032 | 997.5759 | Recommended base = NLR 2025 Mid; use NLR Low/High as the primary battery sensitivities. | 1145.365 | 997.5759 | NLR 2025 Utility-Scale Battery Storage — Mid
BESS 6h | 1705.0128 | 2156.8719 | 1682.1483 | 2679.0906 |  |  |  | 1576.6929 | 1991.6324 | 1545.2026 | 2591.2784 |  | Recommended base = ERCOT LTSA; alternate duration, while 4h remains the preferred core storage case. | 1705.0128 | 1576.6929 | ERCOT 2026 LTSA
How to read this table
The recommended base is technology-specific; see columns O:Q and Recommended_CEM_Base. ERCOT LTSA is not treated as the central source for every technology.
EIA TRE is a current regional anchor, not an explicit 2030/2035 forecast. LBNL is an empirical historical calibration.
The CEM_BaseCase tab is retained only as the all-ERCOT-LTSA benchmark; the title inside that sheet now makes this distinction explicit.

## CEM_BaseCase
ERCOT LTSA Uniform-CAPEX Benchmark — 2030 / 2035 (Real 2025$)
Benchmark only: this sheet applies ERCOT LTSA CAPEX across technologies. Use Recommended_CEM_Base for the preferred technology-specific base case and HOPE_CostProfiles for model-formatted costs.
Technology | Economic life (yr) | Real WACC | 2030 CAPEX (2025$/kW) | CRF | 2030 annualized CAPEX (2025$/kW-yr) | 2030 FOM (2025$/kW-yr) | 2030 total fixed (2025$/kW-yr) | VOM (2025$/MWh) | Heat rate (Btu/kWh) | 2035 CAPEX (2025$/kW) | 2035 annualized CAPEX (2025$/kW-yr) | 2035 FOM (2025$/kW-yr) | 2035 total fixed (2025$/kW-yr) | CAPEX source | O&M source | Modeling note
CC multi-shaft | 30 | 7% | 1314.8599 | 0.080586 | 105.9598 | 12.69 | 118.6498 | 3.57 | 6226 | 1254.1144 | 101.0646 | 12.69 | 113.7546 | ERCOT 2026 LTSA | EIA AEO2026; held constant in real 2025$ unless changed | Base CAPEX = ERCOT LTSA; O&M/performance = EIA multi-shaft CC.
Advanced CT | 30 | 7% | 1193.778 | 0.080586 | 96.2023 | 7.18 | 103.3823 | 4.17 | 9142 | 1109.3161 | 89.3958 | 7.18 | 96.5758 | ERCOT 2026 LTSA | EIA AEO2026; held constant in real 2025$ unless changed | Base CAPEX = ERCOT LTSA; O&M/performance = EIA industrial-frame CT.
ICE | 30 | 7% | 2102.3408 | 0.080586 | 169.4201 |  | 169.4201 |  |  | 2036.8298 | 164.1408 |  | 164.1408 | ERCOT 2026 LTSA | Not populated — add engine-specific O&M/performance source | ERCOT CAPEX is available, but O&M/heat rate should come from the engine technology selected in the model.
SMR | 60 | 7% | 8608.4759 | 0.071229 | 613.1751 | 127.62 | 740.7951 | 3.32 | 10445 | 8133.6439 | 579.3532 | 127.62 | 706.9732 | ERCOT 2026 LTSA | EIA AEO2026; held constant in real 2025$ unless changed | Large uncertainty; retain ATB Advanced/Moderate/Conservative sensitivities.
Wind | 30 | 7% | 2010.8567 | 0.080586 | 162.0477 | 34.57 | 196.6177 | 0 |  | 1960.4085 | 157.9823 | 34.57 | 192.5523 | ERCOT 2026 LTSA | EIA AEO2026; held constant in real 2025$ unless changed | Use ERCOT LTSA base, but compare with ATB and LBNL ERCOT actual costs.
Solar | 30 | 7% | 1171.3554 | 0.080586 | 94.3953 | 23.6 | 117.9953 | 0 |  | 1052.2012 | 84.7931 | 23.6 | 108.3931 | ERCOT 2026 LTSA | EIA AEO2026; held constant in real 2025$ unless changed | Use ERCOT LTSA base; EIA/LBNL provide useful current-cost checks.
BESS 2h | 15 | 7% | 697.7906 | 0.10979 | 76.6137 | 22.2427 | 98.8563 | 0 |  | 645.157 | 70.8348 | 20.7136 | 91.5484 | ERCOT 2026 LTSA | NLR/NREL ATB Moderate duration-specific O&M | ERCOT LTSA CAPEX + ATB Moderate duration-specific FOM/VOM.
BESS 4h | 15 | 7% | 1200.9532 | 0.10979 | 131.8582 | 35.7567 | 167.6149 | 0 |  | 1110.9249 | 121.9736 | 32.9995 | 154.9731 | ERCOT 2026 LTSA | NLR/NREL ATB Moderate duration-specific O&M | ERCOT LTSA CAPEX + ATB Moderate O&M; newer NLR battery series is a key sensitivity.
BESS 6h | 15 | 7% | 1705.0128 | 0.10979 | 187.2012 | 49.2707 | 236.472 | 0 |  | 1576.6929 | 173.1124 | 45.2854 | 218.3978 | ERCOT 2026 LTSA | NLR/NREL ATB Moderate duration-specific O&M | ERCOT LTSA CAPEX + ATB Moderate duration-specific FOM/VOM.
Annualization method
CRF = r(1+r)^n / [(1+r)^n - 1]. Annualized CAPEX = real-2025$ CAPEX × CRF. Total fixed = annualized CAPEX + FOM.
The 7% real WACC and economic lives are editable assumptions on the Assumptions sheet; they are not source facts.
For direct CEM import, the 2030 columns D/F/G/H/I/J and 2035 columns K/L/M/N are the main outputs.

## HOPE_CostProfiles
HOPE-Compatible ERCOT Candidate Cost Profiles — Recommended Hybrid Base
Columns A:U follow the current HOPE candidate_resource_costs_2035.csv schema. Fixed costs now link to Recommended_CEM_Base (technology-specific source selection). Thermal/nuclear fuel-price cells remain editable because fuel price is separate from capital-cost selection.
Type | ApplyToExistingCandidates | CostDollarPerMWYr | CostDollarPerMWh | CapexDollarPerKW | FixedOMDollarPerKWYr | RealDiscountRate | FixedChargeRate | EconomicLifeYears | ProjectionYear | ATBDollarYear | TargetDollarYear | CPIConversionFactor | ATBTechnology | ATBTechDetail | ATBScenario | ATBFinancialCase | FuelPriceDollarPerMMBtu | HeatRateMMBtuPerMWh | SourceURL | SourceNote | DurationHours [helper] | ReadyForDirectHOPE [helper] | VariableCostStatus [helper]
NGCC | 1 | 118649.8331 |  | 1314.8599 | 12.69 | 7% | 8.059% | 30 | 2030 |  | 2025 | 1 | Recommended hybrid | NGCC | Technology-specific base | 7% real CRF |  | 6.226 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ERCOT LTSA. Enter fuel price in column R before direct run; variable cost = VOM + fuel × heat rate. |  | NO | Fuel price / heat rate needed
NGCT | 1 | 103382.2768 |  | 1193.778 | 7.18 | 7% | 8.059% | 30 | 2030 |  | 2025 | 1 | Recommended hybrid | NGCT | Technology-specific base | 7% real CRF |  | 9.142 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ERCOT LTSA. Enter fuel price in column R before direct run; variable cost = VOM + fuel × heat rate. |  | NO | Fuel price / heat rate needed
ICE | 1 |  |  | 2102.3408 |  | 7% | 8.059% | 30 | 2030 |  | 2025 | 1 | Recommended hybrid | ICE | Technology-specific base | 7% real CRF |  |  | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ERCOT LTSA. Enter fuel price in column R before direct run; variable cost = VOM + fuel × heat rate. |  | NO | FOM needed
NuC | 1 | 740795.0692 |  | 8608.4759 | 127.62 | 7% | 7.123% | 60 | 2030 |  | 2025 | 1 | Recommended hybrid | NuC | Technology-specific base | 7% real CRF |  | 10.445 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ERCOT LTSA central + ATB sensitivity. Enter fuel price in column R before direct run; variable cost = VOM + fuel × heat rate. |  | NO | Fuel price / heat rate needed
WindOn | 0 | 157009.1988 | 0 | 1548.8568 | 32.1924 | 7% | 8.059% | 30 | 2030 |  | 2025 | 1 | Recommended hybrid | WindOn | Technology-specific base | 7% real CRF | 0 | 0 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ATB Moderate Wind Class 1. Variable cost uses the recommended-sheet VOM. |  | YES | Ready
SolarPV | 0 | 117995.3219 | 0 | 1171.3554 | 23.6 | 7% | 8.059% | 30 | 2030 |  | 2025 | 1 | Recommended hybrid | SolarPV | Technology-specific base | 7% real CRF | 0 | 0 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ERCOT LTSA. Variable cost uses the recommended-sheet VOM. |  | YES | Ready
Battery | 0 | 98856.3421 | 0 | 697.7906 | 22.2427 | 7% | 10.98% | 15 | 2030 |  | 2025 | 1 | Recommended hybrid | Battery_2h | Technology-specific base | 7% real CRF | 0 | 0 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ERCOT LTSA. Variable cost uses the recommended-sheet VOM. Current HOPE generic storage setup uses 4-hour storage. | 2 | YES | Ready
Battery | 1 | 161511.6149 | 0 | 1145.365 | 35.7567 | 7% | 10.98% | 15 | 2030 |  | 2025 | 1 | Recommended hybrid | Battery_4h | Technology-specific base | 7% real CRF | 0 | 0 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = NLR 2025 Mid. Variable cost uses the recommended-sheet VOM. | 4 | YES | Ready
Battery | 0 | 236471.9521 | 0 | 1705.0128 | 49.2707 | 7% | 10.98% | 15 | 2030 |  | 2025 | 1 | Recommended hybrid | Battery_6h | Technology-specific base | 7% real CRF | 0 | 0 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ERCOT LTSA. Variable cost uses the recommended-sheet VOM. Current HOPE generic storage setup uses 4-hour storage. | 6 | YES | Ready
NGCC | 1 | 113754.5697 |  | 1254.1144 | 12.69 | 7% | 8.059% | 30 | 2035 |  | 2025 | 1 | Recommended hybrid | NGCC | Technology-specific base | 7% real CRF |  | 6.226 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ERCOT LTSA. Enter fuel price in column R before direct run; variable cost = VOM + fuel × heat rate. |  | NO | Fuel price / heat rate needed
NGCT | 1 | 96575.7932 |  | 1109.3161 | 7.18 | 7% | 8.059% | 30 | 2035 |  | 2025 | 1 | Recommended hybrid | NGCT | Technology-specific base | 7% real CRF |  | 9.142 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ERCOT LTSA. Enter fuel price in column R before direct run; variable cost = VOM + fuel × heat rate. |  | NO | Fuel price / heat rate needed
ICE | 1 |  |  | 2036.8298 |  | 7% | 8.059% | 30 | 2035 |  | 2025 | 1 | Recommended hybrid | ICE | Technology-specific base | 7% real CRF |  |  | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ERCOT LTSA. Enter fuel price in column R before direct run; variable cost = VOM + fuel × heat rate. |  | NO | FOM needed
NuC | 1 | 706973.1526 |  | 8133.6439 | 127.62 | 7% | 7.123% | 60 | 2035 |  | 2025 | 1 | Recommended hybrid | NuC | Technology-specific base | 7% real CRF |  | 10.445 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ERCOT LTSA central + ATB sensitivity. Enter fuel price in column R before direct run; variable cost = VOM + fuel × heat rate. |  | NO | Fuel price / heat rate needed
WindOn | 0 | 149411.6099 | 0 | 1468.2638 | 31.0895 | 7% | 8.059% | 30 | 2035 |  | 2025 | 1 | Recommended hybrid | WindOn | Technology-specific base | 7% real CRF | 0 | 0 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ATB Moderate Wind Class 1. Variable cost uses the recommended-sheet VOM. |  | YES | Ready
SolarPV | 0 | 108393.1092 | 0 | 1052.2012 | 23.6 | 7% | 8.059% | 30 | 2035 |  | 2025 | 1 | Recommended hybrid | SolarPV | Technology-specific base | 7% real CRF | 0 | 0 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ERCOT LTSA. Variable cost uses the recommended-sheet VOM. |  | YES | Ready
Battery | 0 | 91548.3613 | 0 | 645.157 | 20.7136 | 7% | 10.98% | 15 | 2035 |  | 2025 | 1 | Recommended hybrid | Battery_2h | Technology-specific base | 7% real CRF | 0 | 0 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ERCOT LTSA. Variable cost uses the recommended-sheet VOM. Current HOPE generic storage setup uses 4-hour storage. | 2 | YES | Ready
Battery | 1 | 142527.9476 | 0 | 997.5759 | 32.9995 | 7% | 10.98% | 15 | 2035 |  | 2025 | 1 | Recommended hybrid | Battery_4h | Technology-specific base | 7% real CRF | 0 | 0 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = NLR 2025 Mid. Variable cost uses the recommended-sheet VOM. | 4 | YES | Ready
Battery | 0 | 218397.7601 | 0 | 1576.6929 | 45.2854 | 7% | 10.98% | 15 | 2035 |  | 2025 | 1 | Recommended hybrid | Battery_6h | Technology-specific base | 7% real CRF | 0 | 0 | https://github.com/swang22/PJM_DC_health_study_project/blob/main/scenario_assumptions/candidate_resource_costs_2035.csv | Linked to Recommended_CEM_Base. CAPEX source = ERCOT LTSA. Variable cost uses the recommended-sheet VOM. Current HOPE generic storage setup uses 4-hour storage. | 6 | YES | Ready
HOPE input interpretation
Current HOPE reference | candidate_resource_costs_2035.csv converts CAPEX/FOM/FCR into CostDollarPerMWYr and passes CostDollarPerMWh directly into candidate data.
ERCOT fixed cost | This sheet is already model-formatted: CostDollarPerMWYr = (annualized CAPEX + FOM) × 1000, in $/MW-yr.
Thermal variable cost | Fuel is intentionally not hard-wired. Enter $/MMBtu in column R; column D computes VOM + fuel price × heat rate.
Battery duration | The current HOPE case uses 4-hour generic storage. 2h/6h rows are preserved as alternative ERCOT profiles and require duration-aware candidate rows.

## HOPE_GenCandidate
HOPE gendata_candidate.csv Template — ERCOT 2030 / 2035
Columns A:Y exactly follow the current HOPE gendata_candidate.csv schema. Cost columns are linked to HOPE_CostProfiles. Yellow cells/blank fields are case-specific inputs still needed before direct execution.
ProjectID | Zone | Pmax (MW) | Pmin (MW) | Cost ($/MW/yr) | Cost ($/MWh) | Type | Flag_thermal | Flag_VRE | Flag_mustrun | EF | CC | AF | FOR | Flag_RPS | CO2_ton_MWh | SO2_lb_MWh | SO2_ton_MWh | NOx_lb_MWh | NOx_ton_MWh | HeatInput_MMBtu_MWh | EmissionFactorBasis | QueueStatus | InServiceYear | FuelPrimary | ReadyForDirectHOPE [helper] | RemainingInputs [helper] | CostProfileRow [helper]
ERCOT_NGCC_2030_GENERIC |  |  | 0 | 118649.8331 |  | NGCC | 1 | 0 | 0 |  |  | 1 |  | 0 | [5 empty] | 6.226 | TBD_ERCOT_emission_factors | Generic ERCOT cost template; replace Zone/Pmax/reliability fields with case data | 2030 | Natural Gas | NO | Set Zone, Pmax, CC, AF/profile, FOR; thermal rows also need fuel price and emissions. | 5
ERCOT_NGCT_2030_GENERIC |  |  | 0 | 103382.2768 |  | NGCT | 1 | 0 | 0 |  |  | 1 |  | 0 | [5 empty] | 9.142 | TBD_ERCOT_emission_factors | Generic ERCOT cost template; replace Zone/Pmax/reliability fields with case data | 2030 | Natural Gas | NO | Set Zone, Pmax, CC, AF/profile, FOR; thermal rows also need fuel price and emissions. | 6
ERCOT_ICE_2030_GENERIC |  |  | 0 |  |  | ICE | 1 | 0 | 0 |  |  | 1 |  | 0 | [6 empty] | TBD_ERCOT_emission_factors | Generic ERCOT cost template; replace Zone/Pmax/reliability fields with case data | 2030 | Natural Gas | NO | Set Zone, Pmax, CC, AF/profile, FOR; thermal rows also need fuel price and emissions. | 7
ERCOT_NuC_2030_GENERIC |  |  | 0 | 740795.0692 |  | NuC | 0 | 0 | 0 | 0 |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | zero_direct_operational_emissions | Generic ERCOT cost template; replace Zone/Pmax/reliability fields with case data | 2030 | Nuclear | NO | Set Zone, Pmax, CC, FOR; confirm nuclear variable cost/fuel treatment. | 8
ERCOT_WindOn_2030_GENERIC |  |  | 0 | 157009.1988 | 0 | WindOn | 0 | 1 | 0 | 0 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | zero_direct_operational_emissions | Generic ERCOT cost template; replace Zone/Pmax/reliability fields with case data | 2030 | Wind | NO | Set Zone, Pmax, CC, AF/profile, FOR. | 9
ERCOT_SolarPV_2030_GENERIC |  |  | 0 | 117995.3219 | 0 | SolarPV | 0 | 1 | 0 | 0 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | zero_direct_operational_emissions | Generic ERCOT cost template; replace Zone/Pmax/reliability fields with case data | 2030 | Solar | NO | Set Zone, Pmax, CC, AF/profile, FOR. | 10
ERCOT_NGCC_2035_GENERIC |  |  | 0 | 113754.5697 |  | NGCC | 1 | 0 | 0 |  |  | 1 |  | 0 | [5 empty] | 6.226 | TBD_ERCOT_emission_factors | Generic ERCOT cost template; replace Zone/Pmax/reliability fields with case data | 2035 | Natural Gas | NO | Set Zone, Pmax, CC, AF/profile, FOR; thermal rows also need fuel price and emissions. | 14
ERCOT_NGCT_2035_GENERIC |  |  | 0 | 96575.7932 |  | NGCT | 1 | 0 | 0 |  |  | 1 |  | 0 | [5 empty] | 9.142 | TBD_ERCOT_emission_factors | Generic ERCOT cost template; replace Zone/Pmax/reliability fields with case data | 2035 | Natural Gas | NO | Set Zone, Pmax, CC, AF/profile, FOR; thermal rows also need fuel price and emissions. | 15
ERCOT_ICE_2035_GENERIC |  |  | 0 |  |  | ICE | 1 | 0 | 0 |  |  | 1 |  | 0 | [6 empty] | TBD_ERCOT_emission_factors | Generic ERCOT cost template; replace Zone/Pmax/reliability fields with case data | 2035 | Natural Gas | NO | Set Zone, Pmax, CC, AF/profile, FOR; thermal rows also need fuel price and emissions. | 16
ERCOT_NuC_2035_GENERIC |  |  | 0 | 706973.1526 |  | NuC | 0 | 0 | 0 | 0 |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | zero_direct_operational_emissions | Generic ERCOT cost template; replace Zone/Pmax/reliability fields with case data | 2035 | Nuclear | NO | Set Zone, Pmax, CC, FOR; confirm nuclear variable cost/fuel treatment. | 17
ERCOT_WindOn_2035_GENERIC |  |  | 0 | 149411.6099 | 0 | WindOn | 0 | 1 | 0 | 0 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | zero_direct_operational_emissions | Generic ERCOT cost template; replace Zone/Pmax/reliability fields with case data | 2035 | Wind | NO | Set Zone, Pmax, CC, AF/profile, FOR. | 18
ERCOT_SolarPV_2035_GENERIC |  |  | 0 | 108393.1092 | 0 | SolarPV | 0 | 1 | 0 | 0 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | zero_direct_operational_emissions | Generic ERCOT cost template; replace Zone/Pmax/reliability fields with case data | 2035 | Solar | NO | Set Zone, Pmax, CC, AF/profile, FOR. | 19

## HOPE_StorageCandidate
HOPE storagedata_candidate.csv Template — ERCOT Battery Candidates
Columns A:V exactly follow the current HOPE storagedata_candidate.csv schema. Enter Zone and Max Power; Capacity (MWh) will calculate automatically from the helper duration.
ProjectID | Zone | Type | Capacity (MWh) | Max Power (MW) | Charging efficiency | Discharging efficiency | Cost ($/MW/yr) | Cost ($/MWh) | EF | CO2_ton_MWh | SO2_lb_MWh | SO2_ton_MWh | NOx_lb_MWh | NOx_ton_MWh | HeatInput_MMBtu_MWh | EmissionFactorBasis | CC | Charging Rate | Discharging Rate | QueueStatus | InServiceYear | DurationHours [helper] | ReadyForDirectHOPE [helper] | RemainingInputs [helper]
ERCOT_BATTERY_2H_2030_GENERIC |  | Battery |  |  | 0.85 | 1 | 98856.3421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | generic_storage_zero_direct_emissions |  | 1 | 1 | Generic ERCOT storage cost template | 2030 | 2 | NO | Set Zone, Max Power/build limit, and ERCOT capacity credit (CC).
ERCOT_BATTERY_4H_2030_GENERIC |  | Battery |  |  | 0.85 | 1 | 161511.6149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | generic_storage_zero_direct_emissions |  | 1 | 1 | Generic ERCOT storage cost template | 2030 | 4 | NO | Set Zone, Max Power/build limit, and ERCOT capacity credit (CC).
ERCOT_BATTERY_6H_2030_GENERIC |  | Battery |  |  | 0.85 | 1 | 236471.9521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | generic_storage_zero_direct_emissions |  | 1 | 1 | Generic ERCOT storage cost template | 2030 | 6 | NO | Set Zone, Max Power/build limit, and ERCOT capacity credit (CC).
ERCOT_BATTERY_2H_2035_GENERIC |  | Battery |  |  | 0.85 | 1 | 91548.3613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | generic_storage_zero_direct_emissions |  | 1 | 1 | Generic ERCOT storage cost template | 2035 | 2 | NO | Set Zone, Max Power/build limit, and ERCOT capacity credit (CC).
ERCOT_BATTERY_4H_2035_GENERIC |  | Battery |  |  | 0.85 | 1 | 142527.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | generic_storage_zero_direct_emissions |  | 1 | 1 | Generic ERCOT storage cost template | 2035 | 4 | NO | Set Zone, Max Power/build limit, and ERCOT capacity credit (CC).
ERCOT_BATTERY_6H_2035_GENERIC |  | Battery |  |  | 0.85 | 1 | 218397.7601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | generic_storage_zero_direct_emissions |  | 1 | 1 | Generic ERCOT storage cost template | 2035 | 6 | NO | Set Zone, Max Power/build limit, and ERCOT capacity credit (CC).